## Air Separator Pressure Loss
Estimating Recommended Maximum Flow Rate for Air Separators
Velocity should not exceed 10fps for standard AC and 12fps for ACT separator
TACO | Entre GPM in the YELLOW section and read PD in the BLUE section | [5 empty] | TACO
separator | STD | FLOW | FLOW | PIPE X-section | VELOCITY | Pressure Drop | Catalogue
AC / ACT | Pipe ID | GPM | FT3/S | Area | FPS | Feet W.G. | listed GPM
2 | 2.221 | 135 | 0.30078 | 0.026915 | 11.1751 | 3.2966 | 80 | 80
2.5 | 2.672 | 200 | 0.4456 | 0.038956 | 11.4386 | 3.4539 | 130 | 130
3 | 3.284 | 300 | 0.6684 | 0.058845 | 11.3587 | 3.4058 | 190 | 190
4 | 4.263 | 500 | 1.114 | 0.099159 | 11.2345 | 3.3317 | 330 | 330
5 | 5.305 | 750 | 1.671 | 0.15356 | 10.8819 | 3.1259 | 550 | 550
6 | 6.045 | 1000 | 2.228 | 0.19939 | 11.1744 | 3.2962 | 900 | 900
8 | 8.303 | 1900 | 4.2332 | 0.37616 | 11.2538 | 3.3432 | 1500 | 1500
10 | 10.385 | 3000 | 6.684 | 0.58846 | 11.3586 | 3.4057 | 2600 | 2600
12 | 12.375 | 4300 | 9.5804 | 0.83559 | 11.4655 | 3.4702 | 3400 | 3400
14 | 13.625 | 5200 | 11.5857 | 1.0129 | 11.4379 | 3.4535 | 4700 | 4700
16 | 15.625 | 6800 | 15.1505 | 1.3321 | 11.3732 | 3.4145 | 6000 | 6000
18 | 17.625 | 8500 | 18.9381 | 1.695 | 11.1732 | 3.2954 | 8000 | 8000
20 | 19.625 | 10800 | 24.0625 | 2.1015 | 11.4504 | 3.461 | 10000 | 10000
22 | 21.625 | 13000 | 28.9641 | 2.5516 | 11.3513 | 3.4014
24 | 23.625 | 15500 | 34.5342 | 3.0454 | 11.3397 | 3.3944
26 | 25.625 | 18500 | 41.2182 | 3.5829 | 11.5043 | 3.4937
28 | 27.625 | 21000 | 46.7882 | 4.164 | 11.2365 | 3.3329
30 | 29.625 | 24500 | 54.5862 | 4.7887 | 11.3989 | 3.43
32 | 31.625 | 28000 | 62.3843 | 5.4571 | 11.4317 | 3.4497
34 | 33.625 | 32000 | 71.2963 | 6.1692 | 11.5569 | 3.5257
36 | 35.625 | 36000 | 80.2084 | 6.9249 | 11.5826 | 3.5414
42 | 41.625 | 48000 | 106.9445 | 9.4539 | 11.3122 | 3.378
48 | 47.625 | 62000 | 138.1366 | 12.3758 | 11.1619 | 3.2888
Average velocity & pressure loss for size 2 to 48 inch: |  |  |  |  | 11.3327 | 3.3909
Pipe Cross-Sectional Area = 22/7 x ID/2 x ID/2
Velocity (Speed) in Feet Per Second (FPS) = Flow/Aea = FT3/S / FT2
Pipe ID is for ANSI Schedule STANDARD Steel Pipe Dimensions
Calculating tank acceptance volume @ different pre-charge pressure
Example Data
Pre-charge pressure in psig |  |  |  |  | 12
Precharge pressure in psia |  |  |  |  | 26.7
Total acceptance volume @ ZERO [ 0 ] pre-charge |  |  |  |  | 158 | catalogue CA600
Tank ASME pressure rating in psig |  |  |  |  | 125
Tank ASME pressure rating in psia |  |  |  |  | 139.7
Tank Acceptance volume at: |  |  | 12 |  | 127.8024
MAP acceptance volume |  |  |  |  | 80.89%

## Pipe ID
Blue Figues = Wall Thickness (inch) & Red Figures = Weight (ft/lb)
Weight 'lb/ft' = (OD -- Wall Thickness) x 10.68 x Wall Thickness
PIPE SIZE | O.D.in inches | 5 | 10 | 40 | STD | 80 | XH | PIPE I.D. STD | PIPE I.D. XH
0.125 | 0.405 | 0.035 | 0.049 | 0.068 | 0.068 | 0.095 | 0.095 | 0.337 | 0.31
|  | 0.1383 | 0.1863 | 0.2447 | 0.2447 | 0.3145 | 0.3145
0.25 | 0.54 | 0.049 | 0.065 | 0.088 | 0.088 | 0.119 | 0.119 | 0.452 | 0.421
|  | 0.257 | 0.3297 | 0.4248 | 0.4248 | 0.5351 | 0.5351
0.375 | 0.675 | 0.049 | 0.065 | 0.091 | 0.091 | 0.126 | 0.126 | 0.584 | 0.549
|  | 0.3276 | 0.4235 | 0.5676 | 0.5676 | 0.7388 | 0.7388
0.5 | 0.84 | 0.065 | 0.083 | 0.109 | 0.109 | 0.147 | 0.147 | 0.731 | 0.693
|  | 0.5383 | 0.671 | 0.851 | 0.851 | 1.088 | 1.088
0.75 | 1.05 | 0.065 | 0.083 | 0.113 | 0.113 | 0.154 | 0.154 | 0.937 | 0.896
|  | 0.6838 | 0.8572 | 1.131 | 1.131 | 1.474 | 1.474
1 | 1.315 | 0.065 | 0.109 | 0.133 | 0.133 | 0.179 | 0.179 | 1.182 | 1.136
|  | 0.8678 | 1.404 | 1.679 | 1.679 | 2.172 | 2.172
1.1/4 | 1.66 | 0.065 | 0.109 | 0.14 | 0.14 | 0.191 | 0.191 | 1.52 | 1.469
|  | 1.107 | 1.806 | 2.273 | 2.273 | 2.997 | 2.997
1.1/2 | 1.9 | 0.065 | 0.109 | 0.145 | 0.145 | 0.2 | 0.2 | 1.755 | 1.7
|  | 1.274 | 2.085 | 2.718 | 2.718 | 3.361 | 3.361
2 | 2.375 | 0.065 | 0.109 | 0.154 | 0.154 | 0.218 | 0.218 | 2.221 | 2.157
|  | 1.604 | 2.638 | 3.653 | 3.653 | 5.022 | 5.022
2.1/2 | 2.875 | 0.083 | 0.12 | 0.203 | 0.203 | 0.276 | 0.276 | 2.672 | 2.599
|  | 2.475 | 3.531 | 5.793 | 5.793 | 7.661 | 7.661
3 | 3.5 | 0.083 | 0.12 | 0.216 | 0.216 | 0.3 | 0.3 | 3.284 | 3.2
|  | 3.029 | 4.332 | 7.576 | 7.576 | 10.25 | 10.25
3.1/2 | 4 | 0.083 | 0.12 | 0.226 | 0.226 | 0.318 | 0.318 | 3.774 | 3.682
|  | 3.472 | 4.973 | 9.109 | 9.109 | 12.51 | 12.51
4 | 4.5 | 0.083 | 0.12 | 0.237 | 0.237 | 0.337 | 0.337 | 4.263 | 4.163
|  | 3.915 | 5.613 | 10.79 | 10.79 | 14.98 | 14.98
4.1/2 | 5 |  |  |  | 0.247 |  | 0.355 | 4.753 | 4.645
[5 empty] | 12.53 |  | 17.61
5 | 5.563 | 0.109 | 0.134 | 0.258 | 0.258 | 0.375 | 0.375 | 5.305 | 5.188
|  | 6.349 | 7.77 | 14.62 | 14.62 | 20.78 | 20.78
6 | 6.325 | 0.109 | 0.134 | 0.28 | 0.28 | 0.432 | 0.432 | 6.045 | 5.893
|  | 7.585 | 9.289 | 18.97 | 18.97 | 28.57 | 28.57
7 | 7.625 |  |  |  | 0.301 |  | 0.5 | 7.324 | 7.125
[5 empty] | 23.57 |  | 38.05
8 | 8.625 | 0.109 | 0.148 | 0.322 | 0.322 | 0.5 | 0.5 | 8.303 | 8.125
|  | 9.914 | 13.4 | 28.55 | 28.55 | 43.39 | 43.39
9 | 9.625 |  |  |  | 0.342 |  | 0.5 | 9.283 | 9.125
[5 empty] | 33.9 |  | 48.72
10 | 10.75 | 0.134 | 0.165 | 0.365 | 0.365 | 0.593 | 0.5 | 10.385 | 10.25
|  | 15.19 | 18.7 | 40.48 | 40.48 | 64.33 | 54.74
11 | 11.75 |  |  |  | 0.375 |  | 0.5 | 11.375 | 11.25
[5 empty] | 45.55 |  | 60.07
12 | 12.75 | 0.165 | 0.18 | 0.406 | 0.375 | 0.687 | 0.5 | 12.375 | 12.25
|  | 22.18 | 24.2 | 53.53 | 49.56 | 88.5 | 65.42
14 | 14 |  | 0.25 | 0.437 | 0.375 | 0.75 | 0.5 | 13.625 | 13.5
|  |  | 36.71 | 63.37 | 54.57 | 106.1 | 72.09
16 | 16 |  | 0.25 | 0.5 | 0.375 | 0.843 | 0.5 | 15.625 | 15.5
|  |  | 42.05 | 82.77 | 62.58 | 136.5 | 82.77
18 | 18 |  | 0.25 | 0.562 | 0.375 | 0.937 | 0.5 | 17.625 | 17.5
|  |  | 47.39 | 104.8 | 70.59 | 170.8 | 93.45
20 | 20 |  | 0.25 | 0.593 | 0.375 | 1.031 | 0.5 | 19.625 | 19.5
|  |  | 52.73 | 122.9 | 78.6 | 208.9 | 104.1
22 | 22 |  | 0.25 |  | 0.375 | 1.125 | 0.5 | 21.625 | 21.5
|  |  | 58.07 |  | 86.61 | 250.8 | 114.8
24 | 24 |  | 0.25 | 0.687 | 0.375 | 1.218 | 0.5 | 23.625 | 23.5
|  |  | 63.41 | 171.2 | 94.62 | 296.4 | 125.5
26 | 26 |  | 0.312 |  | 0.375 |  | 0.5 | 25.625 | 25.5
|  |  | 85.6 |  | 102.6 |  | 136.2
28 | 28 |  | 0.312 |  | 0.375 |  | 0.5 | 27.625 | 27.5
|  |  | 92.26 |  | 110.6 |  | 146.8
30 | 30 |  | 0.312 |  | 0.375 |  | 0.5 | 29.625 | 29.5
|  |  | 98.93 |  | 118.6 |  | 157.5
32 | 32 |  | 0.312 | 0.688 | 0.375 |  | 0.5 | 31.625 | 31.5
|  |  | 105.6 | 230.1 | 126.7 |  | 168.2
34 | 34 |  | 0.344 | 0.688 | 0.375 |  | 0.5 | 33.625 | 33.5
|  |  | 123.7 | 244.8 | 134.7 |  | 178.9
36 | 36 |  | 0.312 | 0.75 | 0.375 |  | 0.5 | 35.625 | 35.5
|  |  | 118.9 | 282.3 | 142.7 |  | 189.6
42 | 42 |  |  |  | 0.375 |  | 0.5 | 41.625 | 41.5
[5 empty] | 166.7 |  | 221.6
48 | 48 |  |  |  | 0.375 |  | 0.5 | 47.625 | 47.5
[5 empty] | 190.7 |  | 253.6

## Sch.40 Steel Pipe
ANSI Schedule 40 Steel Pipe Dimensions
Pipe Size (inches) | Diameter (inches) |  | Nominal Thickness (inches) | Transverse Areas (sq. inches) |  |  | Length of Pipe per sq. foot of |  | Volume (Cubic feet pr. foot) | Weight |  | Number of Threads per inch of Screw
| External | Internal |  | External | Internal | Steel | External Surface Feet | Internal Surface Feet |  | (pounds per foot, lb / ft) | (kg/m)
0.125 | 0,41 | 0,27 | 0,07 | 0,13 | 0,06 | 0,07 | 9,43 | 14,20 | 0,0004 | 0,24 | 0,36 | 27
0.25 | 0,54 | 0,36 | 0,09 | 0,23 | 0,10 | 0,13 | 7,07 | 10,49 | 0,0007 | 0,42 | 0,63 | 18
0.375 | 0,68 | 0,49 | 0,09 | 0,36 | 0,19 | 0,17 | 5,66 | 7,75 | 0,0013 | 0,57 | 0,84 | 18
0.5 | 0,84 | 0,62 | 0,11 | 0,55 | 0,30 | 0,25 | 4,55 | 6,14 | 0,0021 | 0,85 | 1,26 | 18
0.75 | 1,05 | 0,82 | 0,11 | 0,87 | 0,53 | 0,33 | 3,64 | 4,64 | 0,0037 | 1,13 | 1,68 | 14
1 | 1,32 | 1,05 | 0,13 | 1,36 | 0,86 | 0,49 | 2,90 | 3,64 | 0,0060 | 1,68 | 2,50 | 14
1 ¼ | 1,66 | 1,38 | 0,14 | 2,16 | 1,50 | 0,67 | 2,30 | 2,77 | 0,0104 | 2,27 | 3,38 | 11 ½
1 ½ | 1,90 | 1,61 | 0,15 | 2,84 | 2,04 | 0,80 | 2,01 | 2,37 | 0,0141 | 2,72 | 4,04 | 11 ½
2 | 2,38 | 2,07 | 0,15 | 4,43 | 3,36 | 1,08 | 1,61 | 1,85 | 0,0233 | 3,65 | 5,43 | 11 ½
2 ½ | 2,88 | 2,47 | 0,20 | 6,49 | 4,79 | 1,70 | 1,33 | 1,55 | 0,0333 | 5,79 | 8,62 | 11 ½
3 | 3,50 | 3,07 | 0,22 | 9,62 | 7,39 | 2,23 | 1,09 | 1,25 | 0,0513 | 7,58 | 11,27 | 8
3 ½ | 4,00 | 3,55 | 0,23 | 12,56 | 9,89 | 2,68 | 0,95 | 1,08 | 0,0687 | 9,11 | 13,56 | 8
4 | 4,50 | 4,03 | 0,24 | 15,90 | 12,73 | 3,17 | 0,85 | 0,95 | 0,0884 | 10,79 | 16,06 | 8
5 | 5,56 | 5,05 | 0,26 | 24,30 | 20,00 | 4,30 | 0,69 | 0,76 | 0,1389 | 14,61 | 21,74 | 8
6 | 6,63 | 6,07 | 0,28 | 34,47 | 28,89 | 5,58 | 0,58 | 0,63 | 0,2006 | 18,97 | 28,23 | 8
8 | 8,63 | 7,98 | 0,32 | 58,42 | 50,02 | 8,40 | 0,44 | 0,48 | 0,3552 | 28,55 | 42,49 | 8
10 | 10,75 | 10,02 | 0,37 | 90,76 | 78,85 | 11,90 | 0,36 | 0,38 | 0,5476 | 40,48 | 60,24 | 8
12 | 12,75 | 11,94 | 0,41 | 127,64 | 111,90 | 15,74 | 0,30 | 0,32 | 0,7763 | 53,60 | 79,77 | 8
14 | 14,00 | 13,13 | 0,44 | 153,94 | 135,30 | 18,64 | 0,27 | 0,28 | 0,9354 | 63,00 | 93,75 | 8
16 | 16,00 | 15,00 | 0,50 | 201,05 | 176,70 | 24,35 | 0,24 | 0,25 | 12230 | 78,00 | 116,08 | 8
18 | 18,00 | 16,88 | 0,56 | 254,85 | 224,00 | 30,85 | 0,21 | 0,23 | 15550 | 105,00 | 156,26 | 8
20 | 20,00 | 18,81 | 0,59 | 314,15 | 278,00 | 36,15 | 0,19 | 0,20 | 19260 | 123,00 | 183,05 | 8
24 | 24,00 | 22,63 | 0,69 | 452,40 | 402,10 | 50,30 | 0,16 | 0,17 | 27930 | 171,00 | 254,48 | 8